[image: image1.wmf] COES-CENACE-CND

 REP-TRE-ISA

 PowerFactory 13.0.225 

 INTERCONEXIÓN  DC  ECUADOR-PERÚ

 Demanda Mínima Avenida Perú

 Perú exporta 110 MW

 Colombia exporta 120 MW

 Project: CO-EC-PE  

 Graphic: Ec-Pe

 Date:   28-Oct-2003 

 Annex: 05.X1.4.00 

Load Flow Balanced

Nodes

Line-Line Voltage, Magnitude [kV]

Voltage, Magnitude [p.u.]

Voltage, Angle [deg]

Branches

Active Power [MW]

Reactive Power [Mvar]

Maximum Loading [%]

51.85

8.05

30.93

-51.85

-6.87

30.93

-135.77

3.93

34.59

135.78

-0.67

34.59

G

~

360.00

47.91

81.07

PauteAB-1-5

G

~

400.00

45.97

78.82

G

~

100.00

11.49

78.82

PauteC-G6-9

PauteC-G10

G

~

87.00

2.21

89.81

G

~

79.80

7.75

67.26

-102.20

23.54

46.23

104.14

-32.95

46.23

0.80

8.79

16.87

-0.76

-26.09

16.87

-42.24

-12.09

30.33

42.83

-19.83

30.33

85.75

-4.90

72.72

-84.69

-3.67

72.72

-55.79

11.16

16.51

55.86

-14.51

16.51

111.25

-1.42

31.69

-108.81

-14.47

31.69

111.25

-1.42

31.69

-108.81

-14.47

31.69

-101.52

-4.94

28.43

102.11

-0.49

28.43

115.02

3.23

32.69

-113.15

-13.92

32.69

-84.53

-0.14

24.00

85.41

-14.78

24.00

129.52

-17.20

95.96

-128.48

21.36

95.96

EDC_138

141.29

1.02

52.35

PAUTE_230

240.85

1.09

52.15

PASCUA_230

232.94

1.06

41.99

MILAGRO_230

234.54

1.07

44.64

CARHUAQ2

227.31

1.03

18.82

S.IDELF_138

140.97

1.02

50.12

MACHALA_69

70.28

1.02

48.73

CHICLAY2

224.58

1.02

14.93

MACHALA_230

235.03

1.07

50.01

PAUTE_138

144.46

1.05

53.53

PIURAO_2

223.26

1.01

9.78

CARHUAQU

10.20

1.02

23.45

MALACAG4

14.35

1.04

13.61

TALARA_2

227.33

1.03

9.68

ZORRITO2

231.84

1.05

1.70

S.IDELF_230

235.30

1.07

49.40

70.28

48.73

DIgSILENT

[image: image2.wmf]0.00

-21.11

 

1

0.00

-21.11

 

1

Ecuador

  

  

  

Peru

  

  

  

-0.00

-112.20

 

5

-0.00

-42.21

 

1

-1.03

0.00

 

-0.21

0.00

 

-110.00

21.45

70.56

110.63

-24.64

70.56

LINEA_DC

108.97

0.00

22.66

-108.97

0.00

22.66

Reactor 4

Peru Conv4

55.00

45.38

0.67

Peru Conv 3

55.00

45.38

0.67

Ecuador Conv4

-54.38

47.64

2.40

lne ECU_IDF_21

108.76

-10.85

53.42

-107.71

6.46

53.42

IDF_MCH_21

55.86

-14.51

16.51

-55.79

11.16

16.51

Ecuador Conv3

-54.38

47.64

2.40

PERU_240DC

ECUADO_AC

236.27

1.07

53.19

PERU__AC

233.03

1.06

-1.26

EC_LINEA

240.45

1.00

0.00

PERULINEA

240.47

1.00

0.00

EC_240DC

MACHALA_230

235.03

1.07

50.01

S.IDELF_230

235.30

1.07

49.40

ZORRITO2

231.84

1.05

1.70

 COES-CENACE-CND

 REP-TRE-ISA

 PowerFactory 13.0.225 

 INTERCONEXIÓN  DC  ECUADOR-PERÚ

 Demanda Mínima Avenida Perú

 Perú exporta 110 MW

 Colombia exporta 120 MW

 Project: CO-EC-PE  

 Graphic: 12-p HVDC

 Date:   28-Oct-2003 

 Annex: 05.X1.4.00 

DIgSILENT


[image: image3.wmf]30.00

23.98

17.96

11.94

5.920

-0.100

[s]

22.01

10.95

-0.112

-11.17

-22.23

-33.29

Edc_G1: Rotor angle with reference to reference machine angle in deg

Esmeraldas_G1: Rotor angle with reference to reference machine angle in deg

PauteB_1_5: Rotor angle with reference to reference machine angle in deg

Trinitaria_G1: Rotor angle with reference to reference machine angle in deg

30.00

23.98

17.96

11.94

5.920

-0.100

[s]

66.56

52.62

38.67

24.72

10.78

-3.170

sym aguaytia: Rotor angle with reference to reference machine angle in deg

sym carhuaqu: Rotor angle with reference to reference machine angle in deg

sym cañdpato: Rotor angle with reference to reference machine angle in deg

sym machupic: Rotor angle with reference to reference machine angle in deg

sym sangaban: Rotor angle with reference to reference machine angle in deg

sym huincog1: Rotor angle with reference to reference machine angle in deg

Co-Ec-Pe 

INTERCONEXION DC PERU - ECUADOR 

Gen_Firel

Demanda Máxima Avenida - Perú exporta 110 MW 

Salida de una unidad de Paute (100 MW) 

  Date:  29-Oct-2003 

  Annex: 05.X1.4.01 /5

DIgSILENT

[image: image4.wmf]30.00

23.98

17.96

11.94

5.920

-0.100

[s]

159.7

143.6

127.5

111.3

95.24

79.13

sym aguaytia: Active Power in MW

sym machupic: Active Power in MW

sym sangaban: Active Power in MW

30.00

23.98

17.96

11.94

5.920

-0.100

[s]

387.3

379.7

372.1

364.5

356.9

349.3

PauteB_1_5: Active Power in MW

Co-Ec-Pe 

INTERCONEXION DC PERU - ECUADOR 

Gen_P

Demanda Máxima Avenida - Perú exporta 110 MW 

Salida de una unidad de Paute (100 MW) 

  Date:  29-Oct-2003 

  Annex: 05.X1.4.01 /4

DIgSILENT

[image: image5.wmf]30.00

23.98

17.96

11.94

5.920

-0.100

[s]

112.8

79.92

47.08

14.24

-18.60

-51.44

lne PIU_CHI_21: Active Power/Terminal i in MW

lne TAL_PIU_21: Active Power/Terminal i in MW

lne TAL_ZOR_21: Active Power/Terminal i in MW

30.00

23.98

17.96

11.94

5.920

-0.100

[s]

110.1

109.7

109.3

108.9

108.5

108.1

LINEA_DC: Active Power/Terminal i in MW

Co-Ec-Pe 

INTERCONEXION DC PERU - ECUADOR 

MW_LINEAS

Demanda Máxima Avenida - Perú exporta 110 MW 

Salida de una unidad de Paute (100 MW) 

  Date:  29-Oct-2003 

  Annex: 05.X1.4.01 /3

DIgSILENT

[image: image6.wmf]30.00

23.98

17.96

11.94

5.920

-0.100

[s]

1.082

1.067

1.052

1.038

1.023

1.008

MACHALA_138: Voltage, Magnitude in p.u.

MACHALA_69: Voltage, Magnitude in p.u.

MILAGRO_230: Voltage, Magnitude in p.u.

30.00

23.98

17.96

11.94

5.920

-0.100

[s]

1.054

1.024

1.00

0.97

0.94

0.91

CHICLAY2: Voltage, Magnitude in p.u.

PIURAO_2: Voltage, Magnitude in p.u.

TALARA_2: Voltage, Magnitude in p.u.

Co-Ec-Pe 

INTERCONEXION DC PERU - ECUADOR 

VOLTAJES

Demanda Máxima Avenida - Perú exporta 110 MW 

Salida de una unidad de Paute (100 MW) 

  Date:  29-Oct-2003 

  Annex: 05.X1.4.01 /2

DIgSILENT

[image: image7.wmf]30.000

23.980

17.960

11.940

5.9199

-0.1000

[s]

127.88

113.81

99.732

85.659

71.586

57.513

JAM_POM_22: Active Power/Terminal i in MW

Co-Ec-Pe 

INTERCONEXION DC PERU - ECUADOR 

Simul3

Demanda Máxima Avenida - Perú exporta 110 MW 

Salida de una unidad de Paute (100 MW) 

  Date:  29-Oct-2003 

  Annex: 05.X1.4.01 /1

DIgSILENT


[image: image8.wmf]30.00

23.98

17.96

11.94

5.920

-0.100

[s]

20.99

15.61

10.22

4.836

-0.549

-5.934

Edc_G1: Rotor angle with reference to reference machine angle in deg

Esmeraldas_G1: Rotor angle with reference to reference machine angle in deg

PauteB_1_5: Rotor angle with reference to reference machine angle in deg

Trinitaria_G1: Rotor angle with reference to reference machine angle in deg

30.00

23.98

17.96

11.94

5.920

-0.100

[s]

73.05

57.75

42.44

27.13

11.83

-3.479

sym aguaytia: Rotor angle with reference to reference machine angle in deg

sym carhuaqu: Rotor angle with reference to reference machine angle in deg

sym cañdpato: Rotor angle with reference to reference machine angle in deg

sym machupic: Rotor angle with reference to reference machine angle in deg

sym sangaban: Rotor angle with reference to reference machine angle in deg

sym huincog1: Rotor angle with reference to reference machine angle in deg

Co-Ec-Pe 

INTERCONEXION DC PERU - ECUADOR 

Gen_Firel

Demanda Máxima Avenida - Perú exporta 110 MW 

Salida de la central de Carhuaquero 

  Date:  29-Oct-2003 

  Annex: 05.X1.4.02 /5

DIgSILENT

[image: image9.wmf]30.00

23.98

17.96

11.94

5.920

-0.100

[s]

181.4

160.8

140.2

119.6

99.01

78.42

sym aguaytia: Active Power in MW

sym machupic: Active Power in MW

sym sangaban: Active Power in MW

30.00

23.98

17.96

11.94

5.920

-0.100

[s]

360.8

360.5

360.1

359.8

359.5

359.2

PauteB_1_5: Active Power in MW

Co-Ec-Pe 

INTERCONEXION DC PERU - ECUADOR 

Gen_P

Demanda Máxima Avenida - Perú exporta 110 MW 

Salida de la central de Carhuaquero 

  Date:  29-Oct-2003 

  Annex: 05.X1.4.02 /4

DIgSILENT

[image: image10.wmf]30.00

23.98

17.96

11.94

5.920

-0.100

[s]

115.8

76.87

37.95

-0.978

-39.90

-78.83

lne PIU_CHI_21: Active Power/Terminal i in MW

lne TAL_PIU_21: Active Power/Terminal i in MW

lne TAL_ZOR_21: Active Power/Terminal i in MW

30.00

23.98

17.96

11.94

5.920

-0.100

[s]

111.4

110.6

109.8

109.0

108.2

107.3

LINEA_DC: Active Power/Terminal i in MW

Co-Ec-Pe 

INTERCONEXION DC PERU - ECUADOR 

MW_LINEAS

Demanda Máxima Avenida - Perú exporta 110 MW 

Salida de la central de Carhuaquero 

  Date:  29-Oct-2003 

  Annex: 05.X1.4.02 /3

DIgSILENT

[image: image11.wmf]30.00

23.98

17.96

11.94

5.920

-0.100

[s]

1.069

1.058

1.047

1.036

1.025

1.014

MACHALA_138: Voltage, Magnitude in p.u.

MACHALA_69: Voltage, Magnitude in p.u.

MILAGRO_230: Voltage, Magnitude in p.u.

30.00

23.98

17.96

11.94

5.920

-0.100

[s]

1.054

1.024

1.00

0.97

0.94

0.91

CHICLAY2: Voltage, Magnitude in p.u.

PIURAO_2: Voltage, Magnitude in p.u.

TALARA_2: Voltage, Magnitude in p.u.

Co-Ec-Pe 

INTERCONEXION DC PERU - ECUADOR 

VOLTAJES

Demanda Máxima Avenida - Perú exporta 110 MW 

Salida de la central de Carhuaquero 

  Date:  29-Oct-2003 

  Annex: 05.X1.4.02 /2

DIgSILENT

[image: image12.wmf]30.000

23.980

17.960

11.940

5.9199

-0.1000

[s]

61.553

61.166

60.779

60.391

60.004

59.616

JAM_POM_22: Active Power/Terminal i in MW

Co-Ec-Pe 

INTERCONEXION DC PERU - ECUADOR 

Simul3

Demanda Máxima Avenida - Perú exporta 110 MW 

Salida de la central de Carhuaquero 

  Date:  29-Oct-2003 

  Annex: 05.X1.4.02 /1

DIgSILENT


